Alternative Solutions

1.What is an Alternative Solution? 2.When is it used?

3.Who prepares it? 4.What should it contain? 5.How to review it.

6.How to accept or reject it. 7.How to appeal it.

8.Case Studies

What	is	it?

OFC definition

Alternative solution means a substitute for an acceptable solution. Acceptable solution means a requirement set out in Division B.

When	is	it	used?

When you cannot comply or chose not to comply.

Who	prepares	it?

Alternative Solutions are required by Division C Sentence 1.3.2.3.(5) “An alternative solution shall bear the signature and seal of a Professional Engineer or Architect, or both.”

What	should	it contain?

An Alternative solution must contain:

The stamp and signature of an architect or an engineer.

A building description,

A description of the area subject to the Alternative solution,

The code reference of the noncompliant area

The functional and objective statements, as found on the OFM web site.

The reasons how the Alternative solution achieves the goals of the functional and objective statement.

How	to	review	it.

For Part 9 issues

|  |  | Maximum impact | -2 | -1 | Compliant | +1 | +2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Containment | Fire separations | 1 |  |  |  |  |  |
|  | Firewalls | 1 |  |  |  |  |  |
|  | Construction type | 1 |  |  |  |  |  |
|  | Interior finishes | 1 |  |  |  |  |  |
|  | Maximum contribution | 1 |  |  |  |  |  |
| Detection | Alarm and detection | 2 |  |  |  |  |  |
|  | Voice communication | 2 |  |  |  |  |  |
|  | Maximum contribution | 2 |  |  |  |  |  |
| Suppression | Sprinklers | 2 |  |  |  |  |  |
|  | Standpipe | 1 |  |  |  |  |  |
|  | Fire fighters elevator | 1 |  |  |  |  |  |
|  | Smoke control | 1 |  |  |  |  |  |
|  | Maximum contribution | 2 |  |  |  |  |  |
| Egress | Interior exits | 1 |  |  |  |  |  |
|  | Exterior exits | 1 |  |  |  |  |  |
|  | Fire escapes | 1 |  |  |  |  |  |
|  | Emergency lighting | 1 |  |  |  |  |  |
|  | Maximum contribution | 1 |  |  |  |  |  |
| Total |  |  |  |  |  |  |  |

Issue is assigned a -2. All items that comply are assigned 0.

How to accept / reject	it.

The Chief fire official has 45 days from receipt to respond to the applicant.	There is no penalty for the CFO in missing this deadline.

Written decision.

If not acceptable, the reasons. The reasons must be based on sound engineering principles.

Don’t be afraid of making a decision.

HiPPO is an acronym for the "highest paid person's opinion" or the "highest paid person in the office." The acronym is used to describe the tendency for lower-paid employees to defer to higher-paid employees when a decision has to be made.

How to appeal it.

If the owner or owner’s agent feels aggrieved by the decision, they can appeal it within 30 days as if it was an Order.

The OFM will conduct a review of the appeal, and their decision can be to

Accept the AS,

Reject the AS.

Modifying the AS

If rejected by the OFM, then it can be further appealed to the Fire Safety Commission.

Case	Studies

Three storey building:

Combustible building,

Basic fire alarm

5 residential suites

One exit that serves the suites.

30 minute floors.

20 minute suite doors

OFC requirement is Sentence 9.5.3.2.(1).

Alternative Solution:

Sprinklered the corridor, and install one sprinkler head into the suite, above the doorway.

Add smoke detection in the corridor.

Self closers on suite doors.

|  |  | Maximum impact | -2 | -1 | Compliant | +1 | +2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Containment | Fire separations | 1 |  |  | 0 |  |  |
|  | Firewalls | 1 |  |  |  |  |  |
|  | Construction type | 1 |  |  | 0 |  |  |
|  | Interior finishes | 1 |  |  | 0 |  |  |
|  | Maximum contribution | 1 |  |  | 0 |  |  |
| Detection | Alarm and detection | 2 |  |  |  | 1 |  |
|  | Voice communication | 2 |  |  |  |  |  |
|  | Maximum contribution | 2 |  |  |  |  |  |
| Suppression | Sprinklers | 2 |  |  |  | 1 |  |
|  | Standpipe | 1 |  |  |  |  |  |
|  | Fire fighters elevator | 1 |  |  |  |  |  |
|  | Smoke control | 1 |  |  |  |  |  |
|  | Maximum contribution | 2 |  |  |  |  |  |
| Egress | Interior exits | 1 | -2 |  |  |  |  |
|  | Exterior exits | 1 |  |  |  |  |  |
|  | Fire escapes | 1 |  |  |  |  |  |
|  | Emergency lighting | 1 |  |  |  |  |  |
|  | Maximum contribution | 1 |  |  |  |  |  |
| Total |  |  | -2 |  |  | 2 |  |

Explosion Venting

Industrial process,

Sprinklered,

Noncombustible construction,

Storage and dispensing of IB flammable liquids (hexane flash point -22oC, boiling point 68 oC).

OFC requirement is Sentence 4.2.9.6.(1)

This requires the construction of explosion panels, explosion proof walls.

Alternative Solution:

Explosion Prevention

Flammable vapour detection,

Multispeed ventilation fans to increase ventilation upon detection of vapours,

Initiating alarms,

Shutting down processes.

|  |  | Maximum impact | -2 | -1 | Compliant | +1 | +2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Containment | Fire separations | 1 |  |  | 0 |  |  |
|  | Firewalls | 1 |  |  |  |  |  |
|  | Construction type | 1 |  |  | 0 |  |  |
|  | Interior finishes | 1 |  |  | 0 |  |  |
|  | Maximum contribution | 1 |  |  | 0 |  |  |
| Detection | Alarm and detection | 2 |  |  |  | 1 |  |
|  | Voice communication | 2 |  |  |  |  |  |
|  | Maximum contribution | 2 |  |  |  |  |  |
| Suppression | Sprinklers | 2 |  |  | 0 |  |  |
|  | Standpipe | 1 |  |  |  |  |  |
|  | Fire fighters elevator | 1 |  |  |  |  |  |
|  | Smoke control | 1 |  |  |  |  |  |
|  | Access | 1 |  |  |  |  |  |
|  | Maximum contribution | 2 |  |  |  |  |  |
| Egress | Interior exits | 1 |  |  |  |  |  |
|  | Exterior exits | 1 |  |  |  |  |  |
|  | Emergency lighting | 1 |  |  |  |  |  |
|  | Maximum contribution | 1 |  |  |  |  |  |
| Quantities | Maximum amounts | 1 |  |  |  | 1 |  |
| Ventilation | Explosion venting | 2 | -2 |  |  |  |  |
|  | General | 1 |  |  |  |  |  |
|  | High volume | 1 |  |  |  | 1 |  |
| Total |  |  | -2 |  |  | 3 |  |

Standpipe and Hose System

OBC requires Fire hose cabinets with 30 m of fire hose within 5 m of an exit. (Article 3.2.9.4.)

Alternative Solution:

Locate riser in exit

Provide 65 mm hose connections

Reasons:

National building code allows it.

Don’t trust the building’s fire hose,

Occupants should not be tempted to be fire fighters